## Sheet1
208-240V
Fuse type: Protistor® Square-body, NH Plain Blade - 690 VAC aR (PSC-URD 690 VAC)
Ratings: Up to 1000A, 500-690 VAC, 80-170 kA IR
Approvals: Tested to IEC 269.4
Other: Double indicator (visual/mechanical), Cd / Pb free, low voltage indicator (50V)
|  |  |  | DIN43620 Full blade fuse |  |  |  |  | DIN43653 - "D08A" notched blades or brackets DIN80 | DIN43653 - "D11A" notched blades DIN110 | "TTF" threaded end | CP cylindrical fuse
Frame | Current [A] | Number of fuses needed | Fuse rating [A] | Fuse size | Fuse catalogue number | Peak let thru current [A] @ 65 kA | Minimum prospective short circuit current [A] @ 5 ms | Peak arc voltage [V] @ 240 Vac | Cat. Number | Cat. Number | Cat. Number | Cat. Number
MR4 | 3 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 | 950 | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 4 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 |  | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 6 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 |  | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 8 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 |  | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 11 | 3 | 20 | 000 | NH000UD69V20PV | 1300 | 80 |  | DN00UB69V20L | - | - | FR14UC69V20T
MR4 | 12 | 3 | 20 | 000 | NH000UD69V20PV | 1300 | 80 |  | DN00UB69V20L | - | - | FR14UC69V20T
MR5 | 18 | 3 | 32 | 000 | NH000UD69V32PV | 1800 | 140 |  | DN00UB69V32L | - | - | FR14UC69V32T
MR5 | 24 | 3 | 40 | 000 | NH000UD69V40PV | 2000 | 160 |  | DN00UB69V40L | - | - | FR14UC69V40T
MR5 | 31 | 3 | 50 | 000 | NH000UD69V50PV | 1400 | 210 |  | DN00UB69V50L | PC30UD69V50D1A | PC30UD69V50TF | FR14UC69V50T
MR6 | 48 | 3 | 80 | 000 | NH000UD69V80PV | 3500 | 370 |  | DN00UB69V80L | PC30UD69V80D1A | PC30UD69V80TF | -
MR6 | 62 | 3 | 100 | 000 | NH000UD69V100PV | 4400 | 550 |  | DN00UB69V100L | PC30UD69V100D1A | PC30UD69V100TF | -
MR7 | 75 | 3 | 200 | 1 | NH1UD69V200PV | 6500 | 1000 |  | PC30UD69V200A | PC30UD69V200D1A | PC30UD69V200TF | -
MR7 | 88 | 3 | 200 | 1 | NH1UD69V200PV | 6500 | 1000 |  | PC30UD69V200A | PC30UD69V200D1A | PC30UD69V200TF | -
MR7 | 105 | 3 | 250 | 1 | NH1UD69V250PV | 8000 | 1400 |  | PC30UD69V250A | PC30UD69V250D1A | PC30UD69V250TF | -
MR8 | 140 | 3 | 315 | 1 | NH1UD69V315PV | 11000 | 2000 |  | PC30UD69V315A | PC30UD69V315D1A | PC30UD69V315TF | -
MR8 | 170 | 3 | 350 | 1 | NH1UD69V350PV | 12000 | 2400 |  | PC30UD69V350A | PC30UD69V350D1A | PC30UD69V350TF | -
MR8 | 205 | 3 | 400 | 1 | NH1UD69V400PV | 14000 | 2800 |  | PC30UD69V400A | PC30UD69V400D1A | PC30UD69V400TF | -
MR9 | 261 | 3 | 500 | 2 | NH2UD69V500PV | 14000 | 3300 |  | PC31UD69V500A | PC31UD69V500D1A | PC31UD69V500TF | -
MR9 | 310 | 3 | 630 | 2 | NH2UD69V630PV | 18000 | 5000 |  | PC31UD69V630A | PC31UD69V630D1A | PC31UD69V630TF | -
380-500V |  | Fuse type: Protistor® Square-body, NH Plain Blade - 690 VAC aR (PSC-URD 690 VAC)
Ratings: Up to 1000A, 500-690 VAC, 80-170 kA IR
Approvals: Tested to IEC 269.4
Other: Double indicator (visual/mechanical), Cd / Pb free, low voltage indicator (50V)
|  |  |  | DIN43620 Full blade fuse |  |  |  |  | DIN43653 - "D08A" notched blades or brackets DIN80 | DIN43653 - "D11A" notched blades DIN110 | "TTF" threaded end | CP cylindrical fuse
Frame | Current [A] | Number of fuses needed | Fuse rating [A] | Fuse size | Fuse catalogue number | Peak let thru current [A] @ 65 kA | Minimum prospective short circuit current [A] @ 5 ms | Peak arc voltage [V] @ 500 Vac | Cat. Number | Cat. Number | Cat. Number | Cat. Number
MR4 | 3 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 | 1320 | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 4 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 |  | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 5 | 3 | 16 | 000 | NH000UD69V16PV | 1000 | 57 |  | DN00UB69V16L | - | - | FR14UC69V16T
MR4 | 8 | 3 | 20 | 000 | NH000UD69V20PV | 1300 | 80 |  | DN00UB69V20L | - | - | FR14UC69V20T
MR4 | 9 | 3 | 20 | 000 | NH000UD69V20PV | 1300 | 80 |  | DN00UB69V20L | - | - | FR14UC69V20T
MR4 | 12 | 3 | 25 | 000 | NH000UD69V25PV | 1400 | 91 |  | DN00UB69V25L | - | - | FR14UC69V25T
MR5 | 16 | 3 | 32 | 000 | NH000UD69V32PV | 1800 | 140 |  | DN00UB69V32L | - | - | FR14UC69V32T
MR5 | 23 | 3 | 40 | 000 | NH000UD69V40PV | 2000 | 160 |  | DN00UB69V40L | - | - | FR14UC69V40T
MR5 | 31 | 3 | 50 | 000 | NH000UD69V50PV | 1400 | 210 |  | DN00UB69V50L | PC30UD69V50D1A | PC30UD69V50TF | FR14UC69V50T
MR6 | 38 | 3 | 63 | 000 | NH000UD69V63PV | 2900 | 300 |  | DN00UB69V63L | PC30UD69V63D1A | PC30UD69V63TF | -
MR6 | 46 | 3 | 80 | 000 | NH000UD69V80PV | 3500 | 370 |  | DN00UB69V80L | PC30UD69V80D1A | PC30UD69V80TF | -
MR6 | 61 | 3 | 100 | 000 | NH000UD69V100PV | 4400 | 550 |  | DN00UB69V100L | PC30UD69V100D1A | PC30UD69V100TF | -
MR7 | 72 | 3 | 200 | 1 | NH1UD69V200PV | 6500 | 1000 |  | PC30UD69V200A | PC30UD69V200D1A | PC30UD69V200TF | -
MR7 | 87 | 3 | 200 | 1 | NH1UD69V200PV | 6500 | 1000 |  | PC30UD69V200A | PC30UD69V200D1A | PC30UD69V200TF | -
MR7 | 105 | 3 | 200 | 1 | NH1UD69V200PV | 6500 | 1000 |  | PC30UD69V200A | PC30UD69V200D1A | PC30UD69V200TF | -
MR8 | 140 | 3 | 250 | 1 | NH1UD69V250PV | 8000 | 1400 |  | PC30UD69V250A | PC30UD69V250D1A | PC30UD69V250TF | -
MR8 | 170 | 3 | 350 | 1 | NH1UD69V350PV | 12000 | 2400 |  | PC30UD69V350A | PC30UD69V350D1A | PC30UD69V350TF | -
MR8 | 205 | 3 | 400 | 1 | NH1UD69V400PV | 14000 | 2800 |  | PC30UD69V400A | PC30UD69V400D1A | PC30UD69V400TF | -
MR9 | 261 | 3 | 500 | 2 | NH2UD69V500PV | 15000 | 3300 |  | PC31UD69V500A | PC31UD69V500D1A | PC31UD69V500TF | -
MR9 | 310 | 3 | 630 | 2 | NH2UD69V630PV | 18000 | 5000 |  | PC31UD69V630A | PC31UD69V630D1A | PC31UD69V630TF