## Mersen kertoimet1
690 VAC | [6 empty] | Fuse Parameters | [5 empty] | Iac in fuse | Data sheet readings | Cyclic factor (1min) |  | Minimum | Fuse details | [9 empty] | Losses with rated current
| Type | IAC | IAC overload 30 s | Inverter efficiency | Fuse size | # fuses in // | A1 | Bv | C1 | Cpe | A'2 |  | including overload | I [A] 1min | <0,26 | Rectifier I2t | In fuse | Un | In | I2t prearc | I2t at Un | I2t at Uac=690V | I2t 2 fuse in s.c. path | Size | Fuse designation | Part number | Data sheet | per fuse [W]
Ch64 | NX 820 6 | 820 | 902 | 0.985 | 84 | 1 | 0.837 | 1.15 | 0.9 | 0.9 | 0.8 | 1 | 820 | 3600 | 0.25056 | 2196000 | 1314.6664 | 690 | 1400 | 205000 | 1400000 | 1400000 | 910000 | 4 | 170M7060 |  | attached | -
Ch64 | NX 1500 6 | 1500 | 1650 | 0.985 | 84 | 1 | 0.837 | 1.15 | 0.9 | 1 | 0.8 | 1 | 1500 | 8500 | 0.19412 | 2196000 | 2164.3897 | 1000 | 2500 | 300000 | 18000000 | 12600000 | 8190000 | 4 | 170M7640 |  | attached | 340
[7 empty] | A1 | Ambient temperature (60C) |  |  | 0.7-1 | 0.837
[7 empty] | Bv | Forced aircooling (3m/s) |  |  | 1-1.25 | 1.15
[7 empty] | C1 | Bus size derating (83&84) |  |  | 0.8-1 | 0.9 | Typical factor for these fuses
[7 empty] | Cpe | High Frequency derating (?) |  |  | 0.6-1 | 0.85 | "Concervative" rating including Switching Freq harmonics
[7 empty] | A'2 | Cyclic loading with continuous cycle |  |  | 0.6-1 | 0.8 | Continuous use, up to 12 stops per day.
Taulukon ehdottamat 3 rinnan NXA08206; sulake 170M8607, 700 A
| Taulukon ehdottamat 3 rinnan NXA51006; sulake 170M8610, 1000 A | [5 empty] | A1 = sqrt(130 -60/130-30)
130 on sulakkeen maksimi lämmönkesto, valmistaja ilmoittaa
60 C on sulakkeen normaali lämpötilakäytön aikana, riippuu ilmankierrosta, asennuspaikasta.
30 on ympäristön lämpötila, valmistaja määräämä
Note on C2: Ari Ristimaki: AFE AC current? Roughly around this value.
Note on D2: Ari Ristimaki: DC-link current for the fuse

## UL Class J-fuses
Vacon 100 AC fed aircooled. aR UL fuse selection table voltage classes 208-240 V and 380-500 V
IL = low overload , 110 % overloadability 1min/10min
IH = high overload, 150% overloadability 1min/10min
Frame | Type | Voltage [V] | Fuse current | Fuses needed/pcs | Fuse designation | Fuse switch | Minimum short circuit current | Maximum short circuit current
|  |  | [A] |  |  |  | [A] | [kA]
MR4 | 0003 2 | 208 - 240 | 10 | 3 | FWP-10B | OS Mini 30J3 | 45 | 200
MR4 | 0004 2 | 208 - 240 | 15 | 3 | FWP-15B | OS Mini 30J3 | 65 | 200
MR4 | 0006 2 | 208 - 240 | 15 | 3 | FWP-15B | OS Mini 30J3 | 65 | 200
MR4 | 0008 2 | 208 - 240 | 20 | 3 | FWP-20B | OS Mini 30J3 | 100 | 200
MR4 | 0011 2 | 208 - 240 | 25 | 3 | FWP-25B | OS Mini 30J3 | 120 | 200
MR4 | 0012 2 | 208 - 240 | 25 | 3 | FWP-25B | OS Mini 30J3 | 120 | 200
MR5 | 0018 2 | 208 - 240 | 35 | 3 | FWP-35B | OS 60GJ3 | 190 | 200
MR5 | 0024 2 | 208 - 240 | 40 | 3 | FWP-40B | OS 60GJ3 | 210 | 200
MR5 | 0031 2 | 208 - 240 | 50 | 3 | FWP-50B | OS 60GJ3 | 290 | 200
MR6 | 0048 2 | 208 - 240 | 70 | 3 | FWP-70B | OS 100GJ3 | 420 | 200
MR6 | 0062 2 | 208 - 240 | 100 | 3 | FWP-100B | OS 100GJ3 | 560 | 200
MR7 | 0075 2 | 208 - 240 | 125 | 3 | FWP-125A | OS 400J3 | 1100 | 200
MR7 | 0088 2 | 208 - 240 | 150 | 3 | FWP-150A | OS 400J3 | 1500 | 200
MR7 | 0105 2 | 208 - 240 | 175 | 3 | FWP-175A | OS 400J3 | 1600 | 200
MR8 | 0140 2 | 208 - 240 | 225 | 3 | FWP-225A | OS 400J3 | 1800 | 200
MR8 | 0170 2 | 208 - 240 | 300 | 3 | FWP-300A | OS 400J3 | 2800 | 200
MR8 | 0205 2 | 208 - 240 | 350 | 3 | FWP-350A | OS 400J3 | 3500 | 200
MR9 | 0261 2 | 208 - 240 | 450 | 3 | FWP-450A | OS 600J3 | 4200 | 200
MR9 | 0310 2 | 208 - 240 | 600 | 3 | FWP-600A | OS 600J3 | 5400 | 200
Frame | Type | Voltage [V] | Fuse current | Fuses needed/pcs | Fuse designation | Fuse switch | Minimum short circuit current | Maximum short circuit current
|  |  | [A] |  |  |  | [A] | [kA]
MR4 | 0003 5 | 380 -500 | 10 | 3 | FWP-10B | OS Mini 30J3 | 45 | 200
MR4 | 0004 5 | 380 -500 | 15 | 3 | FWP-15B | OS Mini 30J3 | 65 | 200
MR4 | 0005 5 | 380 -500 | 15 | 3 | FWP-15B | OS Mini 30J3 | 65 | 200
MR4 | 0008 5 | 380 -500 | 20 | 3 | FWP-20B | OS Mini 30J3 | 100 | 200
MR4 | 0009 5 | 380 -500 | 20 | 3 | FWP-20B | OS Mini 30J3 | 100 | 200
MR4 | 0012 5 | 380 -500 | 35 | 3 | FWP-20B | OS Mini 30J3 | 100 | 200
MR5 | 0016 5 | 380 -500 | 35 | 3 | FWP-35B | OS 60GJ3 | 190 | 200
MR5 | 0023 5 | 380 -500 | 40 | 3 | FWP-40B | OS 60GJ3 | 210 | 200
MR5 | 0031 5 | 380 -500 | 50 | 3 | FWP-50B | OS 60GJ3 | 290 | 200
MR6 | 0038 5 | 380 -500 | 70 | 3 | FWP-70B | OS 100GJ3 | 420 | 200
MR6 | 0046 5 | 380 -500 | 80 | 3 | FWP-80B | OS 100GJ3 | 470 | 200
MR6 | 0061 5 | 380 -500 | 100 | 3 | FWP-100B | OS 100GJ3 | 560 | 200
MR7 | 0072 5 | 380 -500 | 125 | 3 | FWP-125A | OS 400J3 | 1000 | 200
MR7 | 0087 5 | 380 -500 | 150 | 3 | FWP-150A | OS 400J3 | 1100 | 200
MR7 | 0105 5 | 380 -500 | 175 | 3 | FWP-175A | OS 400J3 | 1500 | 200
MR8 | 0140 5 | 380 -500 | 225 | 3 | FWP-225A | OS 400J3 | 1700 | 200
MR8 | 0170 5 | 380 -500 | 300 | 3 | FWP-300A | OS 400J3 | 2800 | 200
MR8 | 0205 5 | 380 -500 | 350 | 3 | FWP-350A | OS 400J3 | 3500 | 200
MR9 | 0261 5 | 380 -500 | 450 | 3 | FWP-450A | OS 600J3 | 4200 | 200
MR9 | 0310 5 | 380 -500 | 600 | 3 | FWP-600A | OS 600J3 | 5400 | 200
Overload cycles